## NCR Register
NON-CONFORMANCE REPORT (NCR) REGISTER
SN | NCR No. | Issue Date | NCR Catogory | NCR Submittal Date | Discipline | PO No. | Lot No. | ACD | NCR Status | Title | Corrective Action | Description of Non-Conformance
23 | CRPO160-NCR-023 | 2026-07-02 | Minor | 2026-07-05 | Structure |  |  | 2026-07-30 | Closed | Weld Joint ID Error |  | During surveillance, weld joints 2 & 4 were shown in Drawing No. 123; however, no weld is required between the beam web and flange.
1 | CRPO160-NCR-024 | 2026-07-02 | Minor | 2026-07-05 | Structure |  |  | 2026-08-01 | Closed | Electrode Exposure Limit Exceeded |  | during site surveillance SMAW Welder was observed tacking with exceeded maximum exposure of eight hours of Welding Electrode. Welding electrodes were issued by Consumable store.
2 | CRPO160-NCR-025 | 2026-07-11 | Minor | 2026-07-13 | Structure |  |  | 2026-08-11 | Open | E&I Support Orientation Incorrect |  | During site surveillance, a SMAW welder was observed using electrodes beyond the 8-hour exposure limit.
3 | CRPO160-NCR-026 | 2026-07-16 | Minor | 2026-07-19 | Structure |  |  | 2026-08-05 | Closed | Support Frame Plate Distortion |  | During fit-up inspection, the E&I support angle was found installed in reverse orientation from the drawing.
4 | CRPO160-NCR-027 | 2026-07-20 | Minor | 2026-07-22 | Structure |  |  | 2026-10-15 | Open | Material Traceability Discrepancy |  | During material receiving inspection, material traceability and documentation discrepancies were identified.
5 | CRPO160-NCR-028 | 2026-07-20 | Minor | 2026-07-21 | Structure |  |  | 2026-08-14 | Open | Temporary Attachment Distance Not Maintained |  | During site surveillance, a temporary attachment cleat was welded 30 mm from the joint bevel edge.
6 | CRPO160-NCR-029 | 2026-07-23 | Minor | 2026-07-23 | Electrical |  |  | 2026-09-24 | Open | Damaged LV Cable Received |  | During material receiving inspection, cable insulation damage was observed on LV cable drums.